## Sheet1
Synergy Controller 2-Point Calibration Calculations Rev B.xls
1 | Note the current Gain (Span) and Offset values for the input then set the Gain to 100% and the offset to 0.
2 | Fill in the Synergy Controller and Reference Values (from Calibrator) in the Yellow boxes below for the two calibration points
3 | Read the new Gain and Offset in green on the right and enter them for the input.
Corrected values show the value expected after the new gain and offset are entered.
|  | Synergy Controller | Reference | Corrected Value
| Point 1 | 101.1 | 102 | 102
| Point 2 | -100 | -99 | -99
[5 empty] | New Gain | New Offset
[5 empty] | 99.95% | 0.95027